INSTRUCTION MANUAL

CARBON MONOXIDE

TYPE RS485

JXBS-3001-CO

VER1.1

WeihaiJXCTElectronicTechnologyCo.,Ltd.

Ⅰ Brief Introduction

1.1 Product Overview

THE CARBON MONOXIDE SENSOR uses the specialized carbon monoxide concentration sensor probe as core detecting device, which has the characteristics of wide measurement range, high precision, good linearity, good versatility, convenient using, easy installation, long transmission distance and moderate price.

1.2 Primary Parameters

TABLE 1   Primary Parameters

| PARAMETERS | TECHNICAL SPECIFICATIONS |
| --- | --- |
| MEASURING RANGE | 0-1000ppm/0-2000ppm |
| MEASURING MODE | Electrochemical |
| PRECISION | 3%F.s |
| WARRANTY PERIOD | 2 years ( Host ) / 1 year ( Sensor ) |
| RESPONSE TIME | less than 15 seconds |
| BAUD RATE | 2400/4800/9600 |
| COMMUNICATION PORT | RS485 |
| POWER SUPPLY | 12-24V DC |
| POWER CONSUMPTION | ≤0.15w |
| OPERATING TEMPERATURE | -30-50 ℃ |
| WORKING HUMIDITY ENVIRONMENT | 15-90%RH |
| CASE SIZE | 110 x 85 x 44mm3 |
| PRESSURE RANGE | 0.9-1.1atm |

1.3 Probe Parameters And Selection

TABLE 2   Probe Parameters And Selection

| NO. | MANUFACTURER | RANGE | RESOLUTION | LIFE |
| --- | --- | --- | --- | --- |
| 1K | CHINA | 1000ppm | 500ppb | >2 years |
| 2K | CHINA | 2000ppm | 500ppb | >2 years |
| 2KJ | HONEYWELL | 2000ppm | 10ppm | >2 years |

1.4 Cross Interference Gas

| TRACER GAS | CONCENTRATION(ppm) | OUTPUT SIGNAL(amount to ppm CO) |
| --- | --- | --- |
| HYDROGEN SULFIDE | 1000 | 0 |
| SULFUR DIOXIDE | 20 | 0 |
| HYDROGEN | 200 | 40 |
| ETHYLENE | 100 | 80 |
| NITRIC OXIDE | 35 | 6 |
| NITROGEN DIOXIDE | 5 | 0 |
| ETHANOL | 1000 | 0 |

1.5 System Frame Diagram

FIGURE 1   SINGLE-ENDED

FIGURE 2   MUTIPLE-ENDED

Ⅱ Hardware Connections

2.1 CHECKING BEFORE INSTALLATION

Check the list of devices before installation:

TABLE 3   List of Devices

| Name | Number |
| --- | --- |
| THE SENSOR DEVICE | 1 |
| 12V POWER ADAPTER（Optional） | 1 |
| WARRANTY CARD / CERTIFICATE | 1 |
| THE USB TO 485 DEVICE（Optional） | 1 |

2.2 Interface Description

Before you wiring and use, please read this article in detail, Improper use may result in irreversible damage to the product.

FIGURE 3   PHYSICAL PICTURE

TABLE 4   Wiring Sequence

|  | Line Color |  | Description |
| --- | --- | --- | --- |
| Power | Brown |  | Power supply Positive ( 12-24V DC ) |
|  | Black |  | Power supply Negative |
| Communication | Yellow ( Gray ) |  | 485-A |
|  | Blue |  | 485-B |

We provide default cable length of 0.6 meters, you can extend the cable yourself according to your needs.

2.3 Gas Detection Holes

The gas detection hole uses a polymer gas membrane to isolate the membrane. This membrane is air- and water-tight and can permeate the gas but block the moisture. Do not destroy this membrane, otherwise it will affect the life of the product.

2.4 Installation Description

The equipment needs to be placed in an environment where there is no wind and no rain. The equipment needs to be installed vertically. The device has two fixed holes with a spacing of 105mm. The size of each fixing hole is 3mm.

FIGURE 4   HOW FIXTURES

Ⅲ Configuration Tool Installation and use

We provide CONFIGURATION TOOL , which can be easily used to test our sensor device.

3.1 Sensor Access Computer

Transmitter can be connected to PC with the RS485 to USB adapter. You can check the COM port number through Device Manager (right click My Computer).

3.2 How To Use Configuration Tool

Please note that this software can only test one device at the same time. After connecting the physical device, click the CONNECT button to read the information. In the UNCONNET state, you can modify BAUD and ADDR in COMMUNICATION SETTINGS.

Under the software, different check boxes can be selected according to different situations. For example, you can choose the GAS option to test the RS485 OXYGEN SENSOR , you can choose the NORMAL option to test the RS485 TEMPERATURE AND HUMIDITY SENSOR .

Ⅳ Communication Protocol

4.1 Communication Basic Parameters

TABLE 5   Communication Basic Parameters

| PARAMETERS | CONTENT |
| --- | --- |
| Protocol | Modbus RTU |
| Data bits | 8 bit |
| Parity bit | No |
| Stop bit | 1 bit |
| Error checking | CRC (redundant loop code) |
| Baud rate | 2400 bps/ 4800 bps/ 9600 bps can be set factory defaults to 9600 bps |

For more information about MODBUS RTU please visit the website"www.modbus.org ".

4.2 Register Address

| Register Address | Plc Configuration Address | Content | Operation |
| --- | --- | --- | --- |
| 0000H | 40001 | Humidity ( Unit 0.1%RH) | Read-Only |
| 0001H | 40002 | Temperature ( Unit 0.1℃) | Read-Only |
| 0006H | 40007 | Carbon Monoxide ( unit 0. 1ppm) | Read-Only |
| 0100H | 40101 | Device Address (0-252) | R/W |
| 0101H | 40102 | Baud Rate (2400/4800/9600) | R/W |

TABLE 6   Register Address

4.3 Communication example

4.3.1 Read Device Address 0x01's Carbon Monoxide Concentration

TABLE 7   Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00 0x06 | 0x00 0x01 | 0x64 | 0x0B |

TABLE 8   Answer Frames

( For example, the reading is 18.9ppm )

| Address Code | Function Code | Returns to The Number Of Valid Bytes | Carbon Monoxide Value | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x02 | 0x00 0xBD | 0x78 | 0x35 |

Carbon Monoxide：

00BD H ( hexadecimal ) =189=> Carbon Monoxide =18.9ppm

4.3.2 Read Device Address 0x01's Temperature And Humidity Value

TABLE 9   Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x00 | 0x00,0x02 | 0xC4 | 0x0B |

TABLE 10   Answer Frame

| Address Code | Function Code | Number Of Valid Bytes | Humidity Value | Temperature Value | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x04 | 0x00 0xFE | 0x00 0xAF | 0xDB | 0xBF |

Temperature：

00AF H ( hexadecimal ) =175=> Temperature =17.5 ℃

Humidity：

00FE H ( hexadecimal ) =254=> Humidity =25.4%RH

4.3.3 Read Device Address 0x01's Temperature And Humidity, Carbon Monoxide Concentration Value

TABLE 11   Inquiry Frame

| Address Code | Function Code | Start Address | Data Length | CRC_L | CRC_H |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x00 | 0x00,0x07 | 0x04 | 0x08 |

TABLE 12   Answer Frame

| Address Code | Function Code | Number Of Valid Bytes | Humidity Value | Temperature Value |
| --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x0E | 0x03 0x14 | 0x01 0x1B |
| 8 Useless Bytes |  | Carbon Monoxide Value | CRC_L | CRC_H |
| 0x00 ... |  | 0x00 0x28 | 0x50 | 0x3B |

Temperature：

011B H ( hexadecimal ) =283=> Temperature =28.3 ℃

Humidity：

0314 H ( hexadecimal ) =788=> Humidity =78.8%RH

Carbon Monoxide：

0028 H ( hexadecimal ) =40=> Carbon Monoxide =4.0ppm